**IEEE 34 Bus system in Simulink**

* Lines are modelled as Three Phase and Single Phase Pi Section Line
* Voltage regulators are modelled and includes LDC
* Runs in discrete domain with Ts=50 µsec
* Initial Tap settings are taken same as the benchmark document

**Regulator Taps and Parameters**

|  |  |  |  |
| --- | --- | --- | --- |
| Regulator ID: | 1 |  |  |
| Line Segment: | 814 - 850 |  |  |
| Phases: | A - B -C |  |  |
| Connection: | 3-Ph,LG |  |  |
| Monitoring Phase: | A-B-C |  |  |
| Bandwidth: | 2.0 volts |  |  |
| PT Ratio: | 120 |  |  |
| Primary CT Rating: | 100 |  |  |
| Compensator Settings: | Ph-A | Ph-B | Ph-C |
| R - Setting: | 2.7 | 2.7 | 2.7 |
| X - Setting: | 1.6 | 1.6 | 1.6 |
| Voltage Level: | 122 | 122 | 122 |
|  |  |  |  |
| Regulator ID: | 2 |  |  |
| Line Segment: | 852 - 832 |  |  |
| Phases: | A - B -C |  |  |
| Connection: | 3-Ph,LG |  |  |
| Monitoring Phase: | A-B-C |  |  |
| Bandwidth: | 2.0 volts |  |  |
| PT Ratio: | 120 |  |  |
| Primary CT Rating: | 100 |  |  |
| Compensator Settings: | Ph-A | Ph-B | Ph-C |
| R - Setting: | 2.5 | 2.5 | 2.5 |
| X - Setting: | 1.5 | 1.5 | 1.5 |
| Voltage Level: | 124 | 124 | 124 |

**Comparison of Steady state voltages and Substation Power**

|  |  |  |  |
| --- | --- | --- | --- |
| **Substation Active Power (KW)** | **Phase a** | **Phase b** | **Phase c** |
| Benchmark | 759.136 | 666.663 | 617.072 |
| Simulink | 767.2 | 662.5 | 621.4 |

|  |  |  |  |
| --- | --- | --- | --- |
| **Substation Reactive Power (KVar)** | **Phase a** | **Phase b** | **Phase c** |
| Benchmark | 171.727 | 90.137 | 28.394 |
| Simulink | 197.3 | 108.7 | 32.46 |

The large difference in substation power is mainly because the loads in simuklink will get converted to constant imoedance loads during dynamic simulation.

|  |  |  |
| --- | --- | --- |
| **Tap Setting** | **Regulator 1** | **Regulator 2** |
| Benchmark | 12 5 5 | 13 11 12 |
| Simulink(Initial) | 12 5 5 | 13 11 12 |
| Simulink(Final) | 12 5 5 | 13 12 12 |

**Phase A Voltage**

****

**Phase B Voltage**

****

**Phase C Voltage**

****

**% Difference in Voltage**

****

|  |  |  |  |
| --- | --- | --- | --- |
| **Max Error pu** | **Phase a** | **Phase b** | **Phase c** |
|  | 0.0239 | 0.0255 | 0.0171 |